Building Consenting Unit

Construction Statement –

Water supply system & above ground sanitary plumbing pipework testing

Send this Statement to: Inspections Team, Building Consenting Unit, Christchurch City Council, PO Box 73013, Christchurch 8154, or email to: codecompliance@ccc.govt.nz.

TO:   Christchurch City Council Building Consent Authority

Issued by: (name of certifying plumber, holding a current licence)

In respect of Building Consent Number: 	At: (project address)

Made by: (building consent applicant)

In relation to: (description of work)

Water supply system

I have been engaged to undertake the plumbing work on the above approved building consent. I hereby certify that the work complies with the building consent and the NZ Building Code, and I have undertaken a pressure test for water tightness in accordance with:

| ☐ | NZBC G12/AS1 7.5.1 (a),(b): By pressurising the pipework to 1500 kpa for a period of not less than 15 minutes for the hot and cold water supply and checking to see that there are no leaks; or |
| --- | --- |
| ☐ | NZBC G12/AS1 7.5.2, NZS 7643 section 9: By pressurising the upvc. pipework to 1.5 times the maximum working pressure for a period of not less than 15 minutes and checking that there are no leaks; or |
| ☐ | NZBC G12 VM1, AS/NZS 3500.1:2018: By pressurising the pipework to 1500 kpa for a period of not less than 30 minutes and checking to see that there are no leaks; or |
| ☐ | By working pressure (only acceptable for solid/liquid fuel heater wet back connections and solar hot water systems pipework) for a period of not less than 15 minutes and checking that there are no leaks. |

| For sanitary fixtures used for personal hygiene, I confirm that the anti-scald device has been set so as to not exceed: |  |
| --- | --- |
| ☐ | 45°C for early childhood centres, schools, old people’s homes, institutions for people with psychiatric or physical disabilities, hospitals. (G12/AS1 6.14.1(a)); or |
| ☐ | 50°C for all other buildings. (G12/AS1 6.14.1(b)) |

| For hot water supply systems, I confirm the required measures to prevent the growth of Legionella bacteria: |  |
| --- | --- |
| ☐ | Hot water supply system has been tested and set in accordance with G12/AS1 6.14.3; or |
| ☐ | Ancillary heating system (solar/heat pump) have been installed and tested in accordance with G12/AS2 3.5.1 ((a), (b) or (c)); or |
| ☐ | Chlorine disinfection, UV sterilization or high temperature system as consented to circulating systems. |

| And I believe on reasonable grounds that the pipework has passed that test. |  |  |
| --- | --- | --- |
| ☐ | All work complies with the NZBC |  |
| ☐ | Building is connected to a site specific allocated water meter |  |
| ☐ | Water meter serial number is: |  |

Above ground sanitary plumbing pipework

| ☐ | Not applicable as the building work does not include above ground sanitary plumbing pipework |
| --- | --- |

All above ground sanitary plumbing pipework has been tested to verify that the system is watertight.

| ☐ | By a water test in accordance with either clause 7.3 of AS/NZS 2032 or clause 15.2 of AS/NZS 3500.2 |
| --- | --- |
| ☐ | By an air test carried out in accordance with either clause 15.3 of AS/NZS 3500.2 or paragraph 8.3 of E1/VM1 |
| ☐ | By a vacuum test in accordance with clause 15.4 of AS/NZS 3500.2 |

Certifying Plumber’s Details

Name:

Registration number:

Qualifications:

Address:

Phone numbers:

work	mobile	home	 fax

Email:

I hereby state that the work prescribed in this consent application has been carried out by me or my employee and that the employee holds:

(select one)

| ☐ | A current licence under part 2, subpart 1 of the Plumbers Gasfitters and Drainlayers Act 2006; or |
| --- | --- |
| ☐ | Is an exempt trainee under Section 13 of the Plumbers Gasfitters and Drainlayers Act 2006 and the work done by that trainee is carried out in accordance with a limited certificate issued by the Board to the trainee under section 14 of the Act. |

I also understand that the Christchurch City Council in accepting this construction statement may be relying on it to issue the code compliance certificate at the completion of the building work.

| Signature of Certifying Plumber: | Date: |
| --- | --- |